## Slide 2: Overview
Introduction
Net AEP of wind farm clusters (WP3.1)
Uncertainty analysis (WP3.2)
Work plan

## Slide 3: 1. Introduction
Objective:
Provide an accurate value of the expected net energy yield from the cluster of wind farms as well as the uncertainty ranges
Period: [M1-M18]
Deliverables:
  Report on procedure for the estimation of the expected net AEP and the associated uncertainty ranges [M18]

## Slide 4: 1. Introduction
WF 3
WF 1
WF 2
Lwakes[V,θ] = Wake losses (WP1)
Lel_WF= Electrical losses (WP2)
LOM = Operation and Mantainance (WP 3.1.2)
LPC = Power curve deviations (WP 3.1.3)
AEPgross (WP 3.1.1)
AEPnet WF = AEPgross* Lwakes[V,θ]* Lel_WF* LOM* LPC
AEPnet cluster = Lel_intraWF *Σ AEPnet WFi
-
Uncertainty analysis (WP3.2)

## Slide 5: 1. Introduction
WP 3.1 – Net energy yield of wind farm clusters | CENER, CRES, ForWind, Strathclyde University, CIEMAT, Statoil, RES
WP 3.1.1 – Gross energy yield | 
WP 3.1.2 – Losses due to Operations and Mantainance | 
WP 3.1.2 – Losses due to deviations between onsite and manufacturer power curve | 
WP 3.2 – Uncertainty analysis of net energy yield | CIEMAT, Strath, CRES, CENER, DTU-Wind Energy, Uporto, ForWind, RES

## Slide 6: 2. Net AEP of wind farm clusters (WP3.1)
WP 3.1.1: Gross energy yield
  Starting point for the final energy yield
  Wind data (Observational / numerical)
  Long term (LT) analysis:
    Significance of the measuring period
    Alternative use of reanalysis data
  Vertical extrapolation:
    In case no available data at hub height
    Data from several heights
AEPgross WF = F (Wind Data, Power Curve, filtering, LT_analysis, shear_exponent)

## Slide 7: 2. Net AEP of wind farm clusters (WP3.1)
WP 3.1.2 Losses due to Operations & Maintenance (OM)
  Critical parameters affecting OM:
    Vulnerability of design
    Weather conditions (average wave height)
    Wind turbine degradation
    Maintenance and access infrastructure
    Site predictability
  Two options depending on data accessibility:
    Direct modeling (expert judgment tools)
    Table of losses based on experience (site classification)
WF layout
Wind data series (WS, wave height…)
WT specifications
Type of maintenance infraestructure
Modeling / Site classification
OM losses + uncertainty

## Slide 8: 2. Net AEP of wind farm clusters (WP3.1)
WP 3.1.3: Deviations between onsite and manufacturer power curve (PC)
  Critical parameters affecting PC deviations:
    Salinity + Corrosion (WP 1.4)
    Turbulence intensity
  Two options depending on data accessibility:
    Direct modeling (stochastic tools)
    Table of losses based on experience (site classification)
Turbulence intensity
Corrosion
Salinity
Modeling / Site classification
PC losses + uncertainty

## Slide 9: 3. Uncertainty analysis (WP3.2)
  Standardize with industry the uncertainty analysis methodology to avoid ambiguity
  Existing related procedures:
    IEC 61400-12 Standard on Power Curve measurement
    IEA Recommended practices on Wind Speed Measurement
    MEASNET guidelines for wind resource assessment
  Identify Long-Term uncertainty components
  Expected output for each wind farm and cluster:
    Long Term AEP uncertainty
    AEP uncertainty in future periods [1 year, 10 years]
  Gaussian approach mostly extended

## Slide 10: 3. Uncertainty analysis (WP3.2)
  Associated to wind speed estimation:
    SAEP = Sensitivity of gross AEP to wind speed [GWh/ms-1]
Concept | Ucomp | U[m/s] | UWS [GWh]
Measurement process / NWP | Umeas /UNWP | UWS0 | UWS = SAEP*UWS0
Long term correlation | ULT |  | 
Variability of the period | Uvar |  | 
Vertical extrapolation | Uver |  | 

## Slide 11: 3. Uncertainty analysis (WP3.2)
Associated to modeling
‘Historic’ AEP uncertainty: U2LT_WF = U2WS + U2modeling
AEP Uncertainty in ‘future’ periods of N years: U2Ny_WF
P50, P75, P90
Concept | Ucomp | Umodeling [GWh]
Wakes | Uwakes | Umodeling
Electrical | Uelect | 
Operation and Maintenance | UOM | 
Power curve degradation | UPC | 
U2Ny_WF = U2LT_WF + AEPnet*0.061*(1/√N)
HISTORIC
FUTURE

## Slide 12: 4. Work plan
M0
M6
M12
M18
WP 3 – Energy yield of wind farm clusters
Run cases and validation
Direct modeling / experimental table
Review processes / models
Protocol interface - inputs/outputs
Identify study cases
Data access (Conf. issues)

## Slide 13
Thank you very much for your attention